How to upgrade a former BRAUMAT V5.x or V6.x to BRAUMAT V7.1

We assume you use new computer hardware and an actual operating system for the upgraded system

and BRAUMAT V7.1 is already installed by using the setup.

1. First copy the windcs from the former computer to the new one and rename it to keep it as a back up

.

2. Copy the windcs once more for the new BRAUMAT V7.1 project folder.

3. Run the BRAUMAT configuration tool BM_Config.

C:\program files (X86)\siemens\braumat\sys\BM_Config.exe

4. Press ‘….’ for the dialog to select the new project path.

5. Select the project folder you just created by cpoying the former windcs.

6. Accept the message to change the project path.

7. The system offers the posibility to have an archive path different form ptoject path, even on a

different drive. So the configuration asks whether you want to select a different archive path.

8. The configuration tool now notices the old system components in the project folder and asks to delet

them. OK starts the conversion.

9. Accept once more to do the deletion.

10. Converion ends with the message of deleted folders and files.

11. The former system knew two different folders for English language.

The new system works with only one English language.

The engineer has to decide which former folder does contain the user created text files.

Texte.1 or texte.10?

12. The system creates a unique project_ID to mark all the project folders which may be located on

different servers.

13. The project-ID has to be distributed from the origin server to all IOSes using the plant configuration

tool ,SiteCfg. So first do/check all the plant configuration, then distribute it to all IOSes.

14. The upgrade is done now. Maybe do additional configuration before ending the BRAUMAT Basic

Configuration tool.

If finished then

- Make the Time-Synchronization from the site-config-Tool for all IOS

- Go to License-Manager and Install Lizens-key if not done yet. 
For V7.1 you need to install V7.0 –Lizens and upgrade V7.1. Then in Lizense-Manager select one license and select License-key, upgrade. Then the two licenses will be one and they are valid. Otherwise Braumat does not detect a license.

- Go to License-Manager on the clients and ensure that the Engineering-license is floating. In License-Manager go to “Edit”, “connect Computer”.
In V7.x you can use Engineering only on one (any!) Station if you have 1 License.

- On the clients ensure that the Engineering-license is floating. In License-Manager go to “Edit”, “connect Computer”. In V7.x you can use Engineering only on one (any!) Station if you have 1 License.

- Before starting Braumat call the site-config and setup all properly

- Check that the communication in Systems settings PC/PC-Interface is set to the appropriate Network-card.

- Check that in c:\Windows\System32\drivers\etc\hosts the IOS is setup properly e.g.

192.168.0.1 IOS01

192.168.0.2 IOS02

- Share all drives to have Network-access by Braumat Group

- Make a password to login on each PC (eg. User01)

- If you have multiple monitors, modify the mouse settings to find it better.

- Switch in Control.ini: ICM3: show manual mode to “on”

- Switch in Control.ini Analog: ;Background color to display value

- ColorValue=0,0,255 for black

ColorValueBk=0,255,0 for green e.g.

- Check Display manual ICM is ok; if not copy the following to controls.ini (on top)

[Global]

;Use following manual bitmap for state picture

;0=gray color, 1=blue color, 2=red color

ManualColor=2

- Change in seqctrl.ini ;General enabling of EOP activation buttons; EOPAdmin=255

- Check Prosched.ini and remove Trend manager and timer-trigger-programs and adapt Path.

- Change in STATUS.INI; Change Color for Negativ-Status; SetColorText_Neg=1

- Copy the content of \PCU.00x\GOP.txt to \PCU.00x\EPE.txt if the file is empty

- For the Client a native installation of Braumat is enough

- Password is now centralized on the Servers on d:\windcs_V7\Admin\

- PCU: Check that in Fifo Type 7 is removed because time sync goes different now.

- Check for free protocol whether it is used and what needed to be migrated.

- Take the file controls.ini from c:\Program Files (x86)\Siemens\Braumat\!BM_Proj\sys\TRENDMAN.INI and copy to the Project-Path Name\sys

- Copy from c:\Program Files (x86)\SIEMENS\Braumat\!BM_Proj\texte.x\ to your Project without overwriting.

- If in the pictures Trends are used from the other Area the following has to be changed

Kurven.exe p Test.ltb ----- Area=2 “test” 0 0 1024 768

- If Qualifax etc. are used, the Step-Protocols changed their size of columns etc.!

- The colors in the picture might change if saved with Biko!

- Check that the correct Logo is coming in the main menu. If not take it from \Programme\Siemens\Braumat\BM_Proj\Bilder\logo.bmp

- Check for Video-Mode relevant pictures are selected in Biko for Video-Mode and in Site-Config it is checked to be video-Mode.

- Additional Apps in the Main-Menu? Change c:\Program Files (x86)\Siemens\Braumat\texte.0\BM_AppCenter.ini (c:\Program Files (x86)\Siemens\Step7\S7BIN\S7tgtopx.exe).

- New Level in  d:\windcs\Admin\bm_levels.ini

- Ensure with settings in recipe.ini that Recipe-Server switch-over is activated and working. Please test it!

- Test the Time-synchronization

- Ensure Synchronize pictures with other IOS in biko.ini CopyFilesToAll=1 has to be switched on.

- Rename in the Folder \spooler.cis DBF to _DBF.

- Open all recipe and save to generate the IDs.

- Shortly before the real switch over take the latest Recipe-changes, Picture-changes, Name-changes (PCU and text.x-Folder)

- copy the most recent Batch-list BALI

- Install the latest SP or Hotfix!

- Navigation through the pictures without errors?

- Remove RCS from Main Menu if not used.

- Copy latest symbolic-file of Simatic-Manager to Braumat \PCU.00x\s7_sym.seq

- ensure that the free protocol is activated if it was before as well

- Time zone is correct?

- Having specific pictures and Text-files on specific PCs

If one Client or Server (Malt etc) requires specific pictures, in Windcs\sys\PCU.001 the folder \Bilder and PCU.00x\Texte can  be specific for this Client. The Batch-list is not yet IOS-specific.

- If SQL was used, go to site-config, Open the server-configuration, check it and save it, that a new file sys\sistar_adp.ini is generated

- If in the two serves 2 different Measurement-Value-List had been used, they have to be merged! E.G. rename the ID of the second Server with ID old + 1000 = ID new. The same for the digital values. And the same in the pictures d:\windcs\TREND\PICTURE\Name.ltw or MTK.ltb

- Ensure in Image Design Tags-Infos are switched on and ensure the correct Tag-Info is displayed (only Tag-Name).

- Start Braumat without Windows-Shell? Change in Braumat Basic-configuration

- Ensure Braumat starts automatic and as Braumat and not “Administrator”.

- For testing: If SQL is used, check on the SQL-Server in rt_batchprog_param that the Data is coming

For free protocol for each AREA Telegram-Typ “6“ should be coming

No free protocol data: SISTAR_API  „[SYSTEM], FormulaModeel=0“

Test-Protocol

Trending
Step-Protocols
Images and navigation of images
Alarms
Order-System
Engineering on all PC ok?
Measurement-description list